## t1
year | HV to GND | LV to GND | HV to LV | measuring_type
2561 | 1.94 | 2.97 | 2.86 | Polarization Index (PI)
2562 | 2.59 | 3.35 | 1.98 | Polarization Index (PI)
2563 | 3.08 | 2.85 | 2.03 | Polarization Index (PI)
2564 | 1.93 | 3.04 | 2.42 | Polarization Index (PI)
2565 | 2.38 | 3.28 | 2.89 | Polarization Index (PI)
2566 | 4.08 | 4.5 | 3.99 | Polarization Index (PI)

## t2
year | tap | H1-H2 : X1-X0 | H2-H3 : X2-X0 | H3-H1 : X3-X0 | measuring_type
2561 | 1 | -0.00187 | -0.00217 | -0.00155 | Transformer Turn Ratio Test (% Error)
2561 | 2 | -0.00175 | -0.00204 | -0.00141 | Transformer Turn Ratio Test (% Error)
2561 | 3 | -0.00182 | -0.00214 | -0.00148 | Transformer Turn Ratio Test (% Error)
2561 | 4 | -0.00151 | -0.00178 | -0.00115 | Transformer Turn Ratio Test (% Error)
2561 | 5 | -0.00137 | -0.00165 | -0.00102 | Transformer Turn Ratio Test (% Error)
2561 | 6 | -0.00125 | -0.00152 | -0.00087 | Transformer Turn Ratio Test (% Error)
2561 | 7 | -0.00079 | 0 | -0.00041 | Transformer Turn Ratio Test (% Error)
2561 | 8 | -0.00097 | -0.00128 | -0.00058 | Transformer Turn Ratio Test (% Error)
2561 | 9 | -0.00083 | -0.00113 | -0.00051 | Transformer Turn Ratio Test (% Error)
2561 | 10 | -0.00068 | -0.00098 | -0.00029 | Transformer Turn Ratio Test (% Error)
2561 | 11 | -0.00056 | -0.00085 | -0.00014 | Transformer Turn Ratio Test (% Error)
2561 | 12 | -0.00039 | -0.00068 | 3e-05 | Transformer Turn Ratio Test (% Error)
2561 | 13 | -0.00022 | -0.00052 | 0.0002 | Transformer Turn Ratio Test (% Error)
2561 | 14 | -7e-05 | -0.00038 | 0.00037 | Transformer Turn Ratio Test (% Error)
2561 | 15 | 0.00124 | 0.00096 | 0.00169 | Transformer Turn Ratio Test (% Error)
2561 | 16 | 0.00024 | -5e-05 | 0.00074 | Transformer Turn Ratio Test (% Error)
2561 | 17 | 0.00043 | 0.00013 | 0.00091 | Transformer Turn Ratio Test (% Error)
2562 | 1 | -0.00186 | -0.00182 | -0.00184 | Transformer Turn Ratio Test (% Error)
2562 | 2 | -0.00177 | 0 | -0.00171 | Transformer Turn Ratio Test (% Error)
2562 | 3 | -0.00164 | -0.00158 | -0.00154 | Transformer Turn Ratio Test (% Error)
2562 | 4 | -0.00139 | -0.00138 | -0.00137 | Transformer Turn Ratio Test (% Error)
2562 | 5 | -0.00136 | -0.00134 | -0.00135 | Transformer Turn Ratio Test (% Error)
2562 | 6 | -0.00121 | -0.0012 | -0.0012 | Transformer Turn Ratio Test (% Error)
2562 | 7 | -0.00108 | 0 | -0.00108 | Transformer Turn Ratio Test (% Error)
2562 | 8 | -0.00096 | -0.00093 | -0.00092 | Transformer Turn Ratio Test (% Error)
2562 | 9 | -0.0008 | -0.00081 | -0.00077 | Transformer Turn Ratio Test (% Error)
2562 | 10 | -0.00069 | -0.00063 | -0.00062 | Transformer Turn Ratio Test (% Error)
2562 | 11 | -0.00051 | -0.00049 | -0.00049 | Transformer Turn Ratio Test (% Error)
2562 | 12 | 0 | -0.00031 | -0.00037 | Transformer Turn Ratio Test (% Error)
2562 | 13 | -0.00019 | -0.00019 | -0.00016 | Transformer Turn Ratio Test (% Error)
2562 | 14 | -1e-05 | -1e-05 | 2e-05 | Transformer Turn Ratio Test (% Error)
2562 | 15 | 0.00012 | 0.00013 | 0.0002 | Transformer Turn Ratio Test (% Error)
2562 | 16 | 0.0003 | 0.00034 | 0.00039 | Transformer Turn Ratio Test (% Error)
2562 | 17 | 0.0005 | 0.00049 | 0.00056 | Transformer Turn Ratio Test (% Error)
2563 | 1 | -0.00243 | -0.00305 | -8e-05 | Transformer Turn Ratio Test (% Error)
2563 | 2 | -0.00216 | -0.00257 | -0.00045 | Transformer Turn Ratio Test (% Error)
2563 | 3 | -0.00278 | -0.00411 | 0.00208 | Transformer Turn Ratio Test (% Error)
2563 | 4 | -0.00205 | -0.00294 | 0.00078 | Transformer Turn Ratio Test (% Error)
2563 | 5 | -0.00234 | -0.00417 | 0.00245 | Transformer Turn Ratio Test (% Error)
2563 | 6 | -0.00221 | -0.00395 | 0.00251 | Transformer Turn Ratio Test (% Error)
2563 | 7 | -0.00221 | -0.00417 | 0.00321 | Transformer Turn Ratio Test (% Error)
2563 | 8 | -0.00205 | -0.00372 | 0.00292 | Transformer Turn Ratio Test (% Error)
2563 | 9 | -0.00179 | -0.00277 | 0.00214 | Transformer Turn Ratio Test (% Error)
2563 | 10 | -0.00154 | -0.00253 | 0.00209 | Transformer Turn Ratio Test (% Error)
2563 | 11 | -0.00142 | -0.0023 | 0.00216 | Transformer Turn Ratio Test (% Error)
2563 | 12 | -0.00045 | -0.00048 | -0.00017 | Transformer Turn Ratio Test (% Error)
2563 | 13 | -0.00037 | -0.00044 | 0.00013 | Transformer Turn Ratio Test (% Error)
2563 | 14 | -8e-05 | -0.00011 | 8e-05 | Transformer Turn Ratio Test (% Error)
2563 | 15 | 0.00011 | 0.0001 | 0.00014 | Transformer Turn Ratio Test (% Error)
2563 | 16 | -0.00013 | -0.00027 | 0.0013 | Transformer Turn Ratio Test (% Error)
2563 | 17 | 0.0005 | 0.00039 | 0.00054 | Transformer Turn Ratio Test (% Error)
2564 | 1 | -0.00204 | -0.00213 | -0.0017 | Transformer Turn Ratio Test (% Error)
2564 | 2 | -0.00188 | -0.00197 | -0.00166 | Transformer Turn Ratio Test (% Error)
2564 | 3 | -0.00175 | -0.00179 | -0.00156 | Transformer Turn Ratio Test (% Error)
2564 | 4 | -0.00154 | -0.00156 | -0.00136 | Transformer Turn Ratio Test (% Error)
2564 | 5 | -0.00151 | -0.00161 | -0.00126 | Transformer Turn Ratio Test (% Error)
2564 | 6 | -0.00138 | -0.00146 | -0.00118 | Transformer Turn Ratio Test (% Error)
2564 | 7 | -0.00125 | -0.00128 | -0.00101 | Transformer Turn Ratio Test (% Error)
2564 | 8 | -0.00112 | -0.00121 | -0.00084 | Transformer Turn Ratio Test (% Error)
2564 | 9 | -0.00097 | -0.00103 | -0.00075 | Transformer Turn Ratio Test (% Error)
2564 | 10 | -0.00285 | -0.00449 | 0.00489 | Transformer Turn Ratio Test (% Error)
2564 | 11 | -0.00065 | -0.00071 | -0.0005 | Transformer Turn Ratio Test (% Error)
2564 | 12 | -0.00052 | -0.00056 | -0.00033 | Transformer Turn Ratio Test (% Error)
2564 | 13 | -0.00042 | -0.00055 | 3e-05 | Transformer Turn Ratio Test (% Error)
2564 | 14 | -0.00019 | -0.00024 | 1e-05 | Transformer Turn Ratio Test (% Error)
2564 | 15 | -0.00037 | -0.00011 | 8e-05 | Transformer Turn Ratio Test (% Error)
2564 | 16 | -0.00052 | 0.0001 | 0.00013 | Transformer Turn Ratio Test (% Error)
2564 | 17 | -0.00109 | 0.00023 | 0.00018 | Transformer Turn Ratio Test (% Error)
2565 | 1 | -0.0018 | -0.0019 | -0.0019 | Transformer Turn Ratio Test (% Error)
2565 | 2 | -0.0017 | -0.0017 | -0.0017 | Transformer Turn Ratio Test (% Error)
2565 | 3 | -0.0016 | -0.0016 | -0.0016 | Transformer Turn Ratio Test (% Error)
2565 | 4 | -0.0014 | -0.0014 | -0.0014 | Transformer Turn Ratio Test (% Error)
2565 | 5 | -0.0013 | -0.0014 | -0.0014 | Transformer Turn Ratio Test (% Error)
2565 | 6 | -0.0012 | -0.0023 | -0.0013 | Transformer Turn Ratio Test (% Error)
2565 | 7 | -0.0011 | -0.0011 | -0.0011 | Transformer Turn Ratio Test (% Error)
2565 | 8 | -0.0009 | -0.001 | -0.001 | Transformer Turn Ratio Test (% Error)
2565 | 9 | -0.0008 | -0.0009 | -0.0008 | Transformer Turn Ratio Test (% Error)
2565 | 10 | -0.0007 | -0.0008 | -0.0007 | Transformer Turn Ratio Test (% Error)
2565 | 11 | -0.0005 | -0.0006 | -0.0006 | Transformer Turn Ratio Test (% Error)
2565 | 12 | -0.0004 | -0.0004 | -0.0004 | Transformer Turn Ratio Test (% Error)
2565 | 13 | -0.0002 | -0.0026 | -0.0002 | Transformer Turn Ratio Test (% Error)
2565 | 14 | 0 | -0.0001 | -0.0001 | Transformer Turn Ratio Test (% Error)
2565 | 15 | 0.0001 | 0.0001 | 0.0001 | Transformer Turn Ratio Test (% Error)
2565 | 16 | -0.0009 | 0.0002 | 0.0002 | Transformer Turn Ratio Test (% Error)
2565 | 17 | -0.002 | 0.0004 | 0.0004 | Transformer Turn Ratio Test (% Error)
2566 | 1 | -0.0018 | -0.0017 | -0.0018 | Transformer Turn Ratio Test (% Error)
2566 | 2 | -0.0017 | -0.0016 | -0.0017 | Transformer Turn Ratio Test (% Error)
2566 | 3 | -0.0016 | -0.0015 | -0.0015 | Transformer Turn Ratio Test (% Error)
2566 | 4 | -0.0014 | -0.0013 | -0.0013 | Transformer Turn Ratio Test (% Error)
2566 | 5 | -0.0013 | -0.0012 | -0.0013 | Transformer Turn Ratio Test (% Error)
2566 | 6 | -0.0012 | -0.0011 | -0.0012 | Transformer Turn Ratio Test (% Error)
2566 | 7 | -0.0011 | -0.001 | -0.0009 | Transformer Turn Ratio Test (% Error)
2566 | 8 | -0.0009 | -0.0009 | -0.0009 | Transformer Turn Ratio Test (% Error)
2566 | 9 | -0.0008 | -0.0007 | -0.0008 | Transformer Turn Ratio Test (% Error)
2566 | 10 | -0.0006 | -0.0006 | -0.0006 | Transformer Turn Ratio Test (% Error)
2566 | 11 | -0.0005 | -0.0004 | -0.0005 | Transformer Turn Ratio Test (% Error)
2566 | 12 | -0.0003 | -0.0003 | -0.0003 | Transformer Turn Ratio Test (% Error)
2566 | 13 | -0.0002 | -0.0001 | -0.0001 | Transformer Turn Ratio Test (% Error)
2566 | 14 | 0 | 0 | 0 | Transformer Turn Ratio Test (% Error)
2566 | 15 | 0.0001 | 0.0002 | 0.0002 | Transformer Turn Ratio Test (% Error)
2566 | 16 | 0.0003 | 0.0004 | 0.0004 | Transformer Turn Ratio Test (% Error)
2566 | 17 | 0.0005 | 0.0006 | 0.0005 | Transformer Turn Ratio Test (% Error)

## t3
year | tap | H1-H2 : X1-X0 | H2-H3 : X2-X0 | H3-H1 : X3-X0 | measuring_type | subtest_type
2561 | 1 | 2.432 | 2.433 | 2.432 | Winding Resistance Test | Primary winding unit in ohm
2561 | 2 | 2.388 | 2.389 | 2.388 | Winding Resistance Test | Primary winding unit in ohm
2561 | 3 | 2.344 | 2.345 | 2.344 | Winding Resistance Test | Primary winding unit in ohm
2561 | 4 | 2.301 | 2.302 | 2.3 | Winding Resistance Test | Primary winding unit in ohm
2561 | 5 | 2.257 | 2.259 | 2.257 | Winding Resistance Test | Primary winding unit in ohm
2561 | 6 | 2.213 | 2.215 | 2.213 | Winding Resistance Test | Primary winding unit in ohm
2561 | 7 | 2.17 | 2.172 | 2.171 | Winding Resistance Test | Primary winding unit in ohm
2561 | 8 | 2.127 | 2.129 | 2.128 | Winding Resistance Test | Primary winding unit in ohm
2561 | 9 | 2.082 | 2.083 | 2.082 | Winding Resistance Test | Primary winding unit in ohm
2561 | 10 | 2.129 | 2.129 | 2.128 | Winding Resistance Test | Primary winding unit in ohm
2561 | 11 | 2.172 | 2.174 | 2.171 | Winding Resistance Test | Primary winding unit in ohm
2561 | 12 | 2.215 | 2.217 | 2.216 | Winding Resistance Test | Primary winding unit in ohm
2561 | 13 | 2.262 | 2.264 | 2.261 | Winding Resistance Test | Primary winding unit in ohm
2561 | 14 | 2.302 | 2.304 | 2.302 | Winding Resistance Test | Primary winding unit in ohm
2561 | 15 | 2.345 | 2.347 | 2.346 | Winding Resistance Test | Primary winding unit in ohm
2561 | 16 | 2.388 | 2.39 | 2.388 | Winding Resistance Test | Primary winding unit in ohm
2561 | 17 | 2.431 | 2.471 | 2.438 | Winding Resistance Test | Primary winding unit in ohm
2562 | 1 | 2.39 | 2.392 | 2.391 | Winding Resistance Test | Primary winding unit in ohm
2562 | 2 | 2.346 | 2.349 | 2.347 | Winding Resistance Test | Primary winding unit in ohm
2562 | 3 | 2.303 | 2.306 | 2.304 | Winding Resistance Test | Primary winding unit in ohm
2562 | 4 | 2.26 | 2.262 | 2.26 | Winding Resistance Test | Primary winding unit in ohm
2562 | 5 | 2.218 | 2.22 | 2.218 | Winding Resistance Test | Primary winding unit in ohm
2562 | 6 | 2.175 | 0 | 2.176 | Winding Resistance Test | Primary winding unit in ohm
2562 | 7 | 2.133 | 2.135 | 2.133 | Winding Resistance Test | Primary winding unit in ohm
2562 | 8 | 2.091 | 2.093 | 2.091 | Winding Resistance Test | Primary winding unit in ohm
2562 | 9 | 2.046 | 2.048 | 2.046 | Winding Resistance Test | Primary winding unit in ohm
2562 | 10 | 2.092 | 2.093 | 2.092 | Winding Resistance Test | Primary winding unit in ohm
2562 | 11 | 2.136 | 2.136 | 2.134 | Winding Resistance Test | Primary winding unit in ohm
2562 | 12 | 2.177 | 2.179 | 2.178 | Winding Resistance Test | Primary winding unit in ohm
2562 | 13 | 2.22 | 2.221 | 2.22 | Winding Resistance Test | Primary winding unit in ohm
2562 | 14 | 2.262 | 2.264 | 2.262 | Winding Resistance Test | Primary winding unit in ohm
2562 | 15 | 2.305 | 2.306 | 2.305 | Winding Resistance Test | Primary winding unit in ohm
2562 | 16 | 2.347 | 2.348 | 2.348 | Winding Resistance Test | Primary winding unit in ohm
2562 | 17 | 2.391 | 2.391 | 2.39 | Winding Resistance Test | Primary winding unit in ohm
2563 | 1 | 2.408 | 2.409 | 2.408 | Winding Resistance Test | Primary winding unit in ohm
2563 | 2 | 2.363 | 2.366 | 2.364 | Winding Resistance Test | Primary winding unit in ohm
2563 | 3 | 2.32 | 2.322 | 2.32 | Winding Resistance Test | Primary winding unit in ohm
2563 | 4 | 2.277 | 2.279 | 2.277 | Winding Resistance Test | Primary winding unit in ohm
2563 | 5 | 2.234 | 2.236 | 2.234 | Winding Resistance Test | Primary winding unit in ohm
2563 | 6 | 2.192 | 2.193 | 2.191 | Winding Resistance Test | Primary winding unit in ohm
2563 | 7 | 2.149 | 2.151 | 2.149 | Winding Resistance Test | Primary winding unit in ohm
2563 | 8 | 2.107 | 2.109 | 2.106 | Winding Resistance Test | Primary winding unit in ohm
2563 | 9 | 2.061 | 2.063 | 2.061 | Winding Resistance Test | Primary winding unit in ohm
2563 | 10 | 2.107 | 2.108 | 2.107 | Winding Resistance Test | Primary winding unit in ohm
2563 | 11 | 2.15 | 2.152 | 2.15 | Winding Resistance Test | Primary winding unit in ohm
2563 | 12 | 2.193 | 2.195 | 2.193 | Winding Resistance Test | Primary winding unit in ohm
2563 | 13 | 2.236 | 2.238 | 2.236 | Winding Resistance Test | Primary winding unit in ohm
2563 | 14 | 2.279 | 2.28 | 2.279 | Winding Resistance Test | Primary winding unit in ohm
2563 | 15 | 2.322 | 2.323 | 2.322 | Winding Resistance Test | Primary winding unit in ohm
2563 | 16 | 2.365 | 2.366 | 2.364 | Winding Resistance Test | Primary winding unit in ohm
2563 | 17 | 2.407 | 2.408 | 2.407 | Winding Resistance Test | Primary winding unit in ohm
2564 | 1 | 2.403 | 2.404 | 2.323 | Winding Resistance Test | Primary winding unit in ohm
2564 | 2 | 2.359 | 2.36 | 2.269 | Winding Resistance Test | Primary winding unit in ohm
2564 | 3 | 2.316 | 2.317 | 2.232 | Winding Resistance Test | Primary winding unit in ohm
2564 | 4 | 2.272 | 2.273 | 2.217 | Winding Resistance Test | Primary winding unit in ohm
2564 | 5 | 2.23 | 2.23 | 2.147 | Winding Resistance Test | Primary winding unit in ohm
2564 | 6 | 2.19 | 2.179 | 2.18 | Winding Resistance Test | Primary winding unit in ohm
2564 | 7 | 2.145 | 2.138 | 2.132 | Winding Resistance Test | Primary winding unit in ohm
2564 | 8 | 2.102 | 2.086 | 2.089 | Winding Resistance Test | Primary winding unit in ohm
2564 | 9 | 2.057 | 2.035 | 2.041 | Winding Resistance Test | Primary winding unit in ohm
2564 | 10 | 2.102 | 2.087 | 2.088 | Winding Resistance Test | Primary winding unit in ohm
2564 | 11 | 2.146 | 2.118 | 2.132 | Winding Resistance Test | Primary winding unit in ohm
2564 | 12 | 2.189 | 2.167 | 2.174 | Winding Resistance Test | Primary winding unit in ohm
2564 | 13 | 2.231 | 2.233 | 2.232 | Winding Resistance Test | Primary winding unit in ohm
2564 | 14 | 2.274 | 2.275 | 2.275 | Winding Resistance Test | Primary winding unit in ohm
2564 | 15 | 2.317 | 2.318 | 2.318 | Winding Resistance Test | Primary winding unit in ohm
2564 | 16 | 2.359 | 2.361 | 2.36 | Winding Resistance Test | Primary winding unit in ohm
2564 | 17 | 2.402 | 2.404 | 2.403 | Winding Resistance Test | Primary winding unit in ohm
2565 | 1 | 2.447 | 2.449 | 2.447 | Winding Resistance Test | Primary winding unit in ohm
2565 | 2 | 2.403 | 2.404 | 2.403 | Winding Resistance Test | Primary winding unit in ohm
2565 | 3 | 2.359 | 2.36 | 2.359 | Winding Resistance Test | Primary winding unit in ohm
2565 | 4 | 2.315 | 2.316 | 2.359 | Winding Resistance Test | Primary winding unit in ohm
2565 | 5 | 2.272 | 2.272 | 2.272 | Winding Resistance Test | Primary winding unit in ohm
2565 | 6 | 2.228 | 2.229 | 2.22 | Winding Resistance Test | Primary winding unit in ohm
2565 | 7 | 2.185 | 2.186 | 2.185 | Winding Resistance Test | Primary winding unit in ohm
2565 | 8 | 2.142 | 2.142 | 2.142 | Winding Resistance Test | Primary winding unit in ohm
2565 | 9 | 2.095 | 2.097 | 2.096 | Winding Resistance Test | Primary winding unit in ohm
2565 | 10 | 2.142 | 2.143 | 2.142 | Winding Resistance Test | Primary winding unit in ohm
2565 | 11 | 2.186 | 2.187 | 2.186 | Winding Resistance Test | Primary winding unit in ohm
2565 | 12 | 2.23 | 2.231 | 2.23 | Winding Resistance Test | Primary winding unit in ohm
2565 | 13 | 2.274 | 2.274 | 2.273 | Winding Resistance Test | Primary winding unit in ohm
2565 | 14 | 2.376 | 2.318 | 2.317 | Winding Resistance Test | Primary winding unit in ohm
2565 | 15 | 2.36 | 2.361 | 2.36 | Winding Resistance Test | Primary winding unit in ohm
2565 | 16 | 2.403 | 2.404 | 2.404 | Winding Resistance Test | Primary winding unit in ohm
2565 | 17 | 2.447 | 2.448 | 2.447 | Winding Resistance Test | Primary winding unit in ohm
2566 | 1 | 2.467 | 2.468 | 2.461 | Winding Resistance Test | Primary winding unit in ohm
2566 | 2 | 2.419 | 2.423 | 2.419 | Winding Resistance Test | Primary winding unit in ohm
2566 | 3 | 2.375 | 2.38 | 2.376 | Winding Resistance Test | Primary winding unit in ohm
2566 | 4 | 2.329 | 2.329 | 2.331 | Winding Resistance Test | Primary winding unit in ohm
2566 | 5 | 2.286 | 2.286 | 2.285 | Winding Resistance Test | Primary winding unit in ohm
2566 | 6 | 2.246 | 2.243 | 2.24 | Winding Resistance Test | Primary winding unit in ohm
2566 | 7 | 2.205 | 2.201 | 2.199 | Winding Resistance Test | Primary winding unit in ohm
2566 | 8 | 2.168 | 2.164 | 2.163 | Winding Resistance Test | Primary winding unit in ohm
2566 | 9 | 2.122 | 2.114 | 2.116 | Winding Resistance Test | Primary winding unit in ohm
2566 | 10 | 2.166 | 2.161 | 2.158 | Winding Resistance Test | Primary winding unit in ohm
2566 | 11 | 2.206 | 2.202 | 2.203 | Winding Resistance Test | Primary winding unit in ohm
2566 | 12 | 2.246 | 2.245 | 2.244 | Winding Resistance Test | Primary winding unit in ohm
2566 | 13 | 2.287 | 2.288 | 2.287 | Winding Resistance Test | Primary winding unit in ohm
2566 | 14 | 2.335 | 2.332 | 2.33 | Winding Resistance Test | Primary winding unit in ohm
2566 | 15 | 2.379 | 2.377 | 2.376 | Winding Resistance Test | Primary winding unit in ohm
2566 | 16 | 2.429 | 2.424 | 2.423 | Winding Resistance Test | Primary winding unit in ohm
2566 | 17 | 2.463 | 2.462 | 2.46 | Winding Resistance Test | Primary winding unit in ohm

## t4
year | H1-H2 : X1-X0 | H2-H3 : X2-X0 | H3-H1 : X3-X0 | measuring_type | subtest_type
2561 | 37.201 | 37.71 | 37.897 | Winding Resistance Test | Secondary winding unit in ohm
2562 | 36.554 | 37.158 | 37.211 | Winding Resistance Test | Secondary winding unit in ohm
2563 | 37.266 | 37.355 | 37.488 | Winding Resistance Test | Secondary winding unit in ohm
2564 | 36.841 | 37.246 | 37.539 | Winding Resistance Test | Secondary winding unit in ohm
2565 | 37.402 | 37.941 | 38.136 | Winding Resistance Test | Secondary winding unit in ohm
2566 | 97.597 | 38.165 | 38.346 | Winding Resistance Test | Secondary winding unit in ohm

## t5
year | Test metod | Oxygen | Nitrogen | Hydrogen | Methane | Carbon monoxide | Carbon dioxide | Ethylene | Ethane | Acetylene | Propylene | Propane | TDCG | measuring_type | subtest_type
2561 | ASTM D 3612 Method C | 8594 | 36840 | 15 | 5 | 212 | 1620 | 2 | 0 | 0 | 0 | 0 | 234 | Dissolved Gas Analysis | Main Tank
2561 | Recommended safe fault gas levels (IEEE C57-104-2008) | - | - | 170 | 850 | 1000 | 10000 | 170 | 850 | 40 | - | - | 3080 | Dissolved Gas Analysis | Main Tank
2562 | ASTM D 3612 Method C | 14548 | 53793 | 10 | 1 | 109 | 1890 | 0 | 0 | 0 | 0 | 0 | 120 | Dissolved Gas Analysis | Main Tank
2562 | Recommended safe fault gas levels (IEEE C57-104-2008) | - | - | 190 | 950 | 1000 | 10000 | 190 | 950 | 45 | - | - | 3325 | Dissolved Gas Analysis | Main Tank
2563 | ASTM D 3612 Method C | 15278 | 44662 | 5 | 6 | 558 | 1639 | 2 | 0 | 0 | 1 | 0 | 571 | Dissolved Gas Analysis | Main Tank
2563 | Recommended safe fault gas levels (IEEE C57-104-2008) | - | - | 210 | 1050 | 1000 | 10000 | 210 | 1050 | 50 | - | - | 3570 | Dissolved Gas Analysis | Main Tank
2564 | ASTM D 3612 Method C | 4325 | 10547 | 0 | 2 | 421 | 1342 | 1 | 0 | 0 | 0 | 0 | 424 | Dissolved Gas Analysis | Main Tank
2564 | Recommended safe fault gas levels (IEEE C57-104-2008) | - | - | 230 | 1150 | 1000 | 10000 | 230 | 1150 | 55 | - | - | 3815 | Dissolved Gas Analysis | Main Tank
2565 | ASTM D 3612 Method C | 2029 | 14786 | 0 | 5 | 296 | 571 | 3 | 2 | 0 | 2 | 1 | 306 | Dissolved Gas Analysis | Main Tank
2565 | Recommended safe fault gas levels (IEEE C57-104-2008) | - | - | 250 | 1250 | 1000 | 10000 | 250 | 1250 | 60 | - | - | 4060 | Dissolved Gas Analysis | Main Tank
2566 | ASTM D 3612 Method C | 6983 | 43529 | 0 | 1 | 64 | 410 | 1 | 1 | 0 | 1 | 1 | 67 | Dissolved Gas Analysis | Main Tank
2566 | Recommended safe fault gas levels (IEEE C57-104-2008) | - | - | 270 | 1350 | 1000 | 10000 | 270 | 1350 | 65 | - | - | 4305 | Dissolved Gas Analysis | Main Tank

## t6
year | Total Pressure (< 1 atm) | O2/N2 (Leak <5) | CO2/CO (paper degradation >3) | measuring_type | subtest_type
2561 | 0.45 | - | 7.64 | Dissolved Gas Analysis | Main Tank (IEC 60599-2015)
2562 | - | - | - | Dissolved Gas Analysis | Main Tank (IEC 60599-2015)
2563 | 0.55 | - | 2.94 | Dissolved Gas Analysis | Main Tank (IEC 60599-2015)
2564 | 0.16 | - | 3.19 | Dissolved Gas Analysis | Main Tank (IEC 60599-2015)
2565 | 0.17 | 0.14 | 1.93 | Dissolved Gas Analysis | Main Tank (IEC 60599-2015)
2566 | 0.49 | 0.16 | 6.42 | Dissolved Gas Analysis | Main Tank (IEC 60599-2015)

## t7
year | test method | Oxygen | Nitrogen | Hydrogen | Methane | Carbon monoxide | Carbon dioxide | Ethylene | Ethane | Acetylene | Propylene | Propane | TDCG | measuring_type | subtest_type
2561 | ASTM D 3612 Method C | 21289 | 42949 | 1605 | 198 | 155 | 616 | 144 | 2 | 220 | 0 | 5 | 2324 | Dissolved Gas Analysis | OLTC
2562 | ASTM D 3612 Method C | 16869 | 45068 | 660 | 25 | 88 | 32 | 30 | 1 | 22 | 1 | 0 | 826 | Dissolved Gas Analysis | OLTC
2563 | ASTM D 3612 Method C | 18168 | 45210 | 986 | 38 | 143 | 63 | 53 | 2 | 51 | 4 | 1 | 1273 | Dissolved Gas Analysis | OLTC
2564 | ASTM D 3612 Method C | 11087 | 24086 | 373 | 24 | 187 | 133 | 40 | 2 | 31 | 3 | 1 | 657 | Dissolved Gas Analysis | OLTC
2565 | ASTM D 3612 Method C | 5498 | 28173 | 690 | 43 | 124 | 117 | 108 | 3 | 68 | 14 | 1 | 1036 | Dissolved Gas Analysis | OLTC
2566 | ASTM D 3612 Method C | 9637 | 59372 | 753 | 43 | 9 | 82 | 9 | 3 | 13 | 2 | 2 | 830 | Dissolved Gas Analysis | OLTC

## t8
year | key_type | CH4 | C2H4 | C2H2 | result | measuring_type | subtest_type
2561 | Keys gas (ppm) | 198 | 144 | 220 | X3 | Dissolved Gas Analysis | OLTC
2561 | Estimate | 35.2313 | 25.6228 | 39.1459 | X3 | Dissolved Gas Analysis | OLTC
2562 | Keys gas (ppm) | 25 | 30 | 22 | X3 | Dissolved Gas Analysis | OLTC
2562 | Estimate | 32.4675 | 38.961 | 28.5714 | X3 | Dissolved Gas Analysis | OLTC
2563 | Keys gas (ppm) | 38 | 53 | 51 | X3 | Dissolved Gas Analysis | OLTC
2563 | Estimate | 26.7606 | 37.3239 | 35.9155 | X3 | Dissolved Gas Analysis | OLTC
2564 | Keys gas (ppm) | 24 | 40 | 31 | X3 | Dissolved Gas Analysis | OLTC
2564 | Estimate | 25.2632 | 42.1053 | 32.6316 | X3 | Dissolved Gas Analysis | OLTC
2565 | Keys gas (ppm) | 43 | 108 | 68 | X3 | Dissolved Gas Analysis | OLTC
2565 | Estimate | 19.6347 | 49.3151 | 31.0502 | X3 | Dissolved Gas Analysis | OLTC
2566 | Keys gas (ppm) | 43 | 9 | 13 | X1 | Dissolved Gas Analysis | OLTC
2566 | Estimate | 66.1538 | 13.8462 | 20 | X1 | Dissolved Gas Analysis | OLTC

## t9
year | Test method | kV | measuring_type | subtest_type
2561 | IEC 60156 | 73 | Dielectric Breakdown Voltage | Main Tank
2562 | IEC 60156 | - | Dielectric Breakdown Voltage | Main Tank
2563 | IEC 60156 | 88 | Dielectric Breakdown Voltage | Main Tank
2564 | IEC 60156 | 95 | Dielectric Breakdown Voltage | Main Tank
2565 | IEC 60156 | - | Dielectric Breakdown Voltage | Main Tank
2566 | IEC 60156 | 60 | Dielectric Breakdown Voltage | Main Tank

## t10
year | Test method | kV | measuring_type | subtest_type
2561 | IEC 60156 | 75 | Dielectric Breakdown Voltage | OLTC
2562 | IEC 60156 | - | Dielectric Breakdown Voltage | OLTC
2563 | IEC 60156 | 80 | Dielectric Breakdown Voltage | OLTC
2564 | IEC 60156 | 95 | Dielectric Breakdown Voltage | OLTC
2565 | IEC 60156 | - | Dielectric Breakdown Voltage | OLTC
2566 | IEC 60156 | 89 | Dielectric Breakdown Voltage | OLTC

## t11
year | Test method | ppm | measuring_type | subtest_type
2561 | ASTM D1533 | 13 | Water content in insulating liquid | Main Tank
2562 | ASTM D1533 | - | Water content in insulating liquid | Main Tank
2563 | ASTM D1533 | 8 | Water content in insulating liquid | Main Tank
2564 | ASTM D1533 | 5 | Water content in insulating liquid | Main Tank
2565 | ASTM D1533 | - | Water content in insulating liquid | Main Tank
2566 | ASTM D1533 | 8 | Water content in insulating liquid | Main Tank

## t12
year | Test method | ppm | measuring_type | subtest_type
2561 | ASTM D1533 | 4 | Water content in insulating liquid | OLTC
2562 | ASTM D1533 | - | Water content in insulating liquid | OLTC
2563 | ASTM D1533 | 6 | Water content in insulating liquid | OLTC
2564 | ASTM D1533 | 5 | Water content in insulating liquid | OLTC
2565 | ASTM D1533 | - | Water content in insulating liquid | OLTC
2566 | ASTM D1533 | 5 | Water content in insulating liquid | OLTC